## TRACKING_ACTION
FACILITY_ID | CIRCUIT | DEV_TYPE | SUBTYPE | INCIDENT_ID | CountOfFACILITY_ID | CAUSE_DESCR | OUTAGE_TIME | CONFIG | CI | INVESTIGATED | Append Date | MONTH REPEATER | YEAR REPEATER | EAST/WEST | NOTES | ASSIGNED PERSON | ACTION TAKEN | COMPLETED | COMPLETED DATE
34468-NONE40481 | 1433 | Fuse | Cutout | 341566 | 3 | Unknown | 2017-11-21 18:49 | OH | 16 | FALSE | 2018-08-28 | FALSE | TRUE | E |  |  |  | FALSE
30576-NONE1161 | 205 | Fuse | Cutout | 353640 | 2 | Weather Lighting | 2018-07-18 16:50 | OH | 2 | TRUE | 2018-08-02 | TRUE | FALSE | E | Patrol needed | OSMAN, DANY, KRIS | Patrolled. No action taken. | TRUE | 2018-08-20
30576-NONE1161 | 205 | Fuse | Cutout | 353841 | 2 | Weather Lighting | 2018-07-22 14:45 | OH | 2 | TRUE | 2018-08-02 | TRUE | FALSE | E | Patrol needed | OSMAN, DANY, KRIS | Patrolled. No action taken. | TRUE | 2018-08-20
35404-FX595L0 | 550 | Fuse | Cutout Terminating | 353538 | 2 | Equip Fail UG Primary | 2018-07-16 10:52 | UG | 108 | TRUE | 2018-08-02 | TRUE | FALSE | W | UG primary burnout same incident with the next one. Nothing to do |  |  | TRUE | 2018-08-13
35404-FX595L0 | 550 | Fuse | Cutout Terminating | 353565 | 2 | Equip Fail UG Primary | 2018-07-16 12:32 | UG | 70 | TRUE | 2018-08-02 | TRUE | FALSE | W | UG primary burnout same incident with the previous one. Nothing to do. |  |  | TRUE | 2018-08-13
1036 | 1036 | Circuit Breaker | Circuit Breaker | 348303 | 4 | Vegetation Tree Non-Preventable | 2018-03-21 18:57 | U | 3505 | TRUE | 2018-08-02 | FALSE | TRUE | W | Osman discussed with Angel. Undergrounding option between poles 22765 and 51335 should be discussed further. Tree trimming between poles 50459 and 20145 will be discussed with Don. 8/10/18 | OSMAN |  | FALSE
1036 | 1036 | Circuit Breaker | Circuit Breaker | 350010 | 4 | Human Dig In Contract Crew | 2018-05-02 13:29 | U | 3488 | TRUE | 2018-08-02 | FALSE | TRUE | W | Contractor dig. Not much to do | N/A |  | FALSE
1036 | 1036 | Circuit Breaker | Circuit Breaker | 352276 | 4 | Weather Lighting | 2018-06-16 15:19 | U | 3506 | TRUE | 2018-08-02 | FALSE | TRUE | W | This is because of relaying. Circuit breaker should have opened after lightining. It did not and then it opened low side breaker. 8/10/18 | OSMAN |  | FALSE
1036 | 1036 | Circuit Breaker | Circuit Breaker | 353837 | 4 | Vegetation Tree Non-Preventable | 2018-07-22 14:41 | U | 3505 | TRUE | 2018-08-02 | FALSE | TRUE | W | Osman discussed with Angel. Undergrounding option between poles 22765 and 51335 should be discussed further. Tree trimming between poles 50459 and 20145 will be discussed with Don. 8/10/18 | OSMAN |  | FALSE
21169-NONE5514 | 211 | Fuse | Cutout | 351740 | 3 | Equip Fail Arrestor | 2018-06-05 05:03 | OH | 13 | TRUE | 2018-08-02 | FALSE | TRUE | E | Patrol needed. Check arrestors and consider more trimming. Bamboo removal between poles 47113 & 21169 was requested 7/2/18. Check if it is removed. 8/10/18 | OSMAN, DANY, KRIS | Patrolled. Sent an email to Don Eyster for trimming. FUWO sent for low secondaries at house# 2230 and 2214. 8/20/18.--Per Joe Wolf trimming cycle is coming soon to this lateral. | TRUE | 2018-08-29
21169-NONE5514 | 211 | Fuse | Cutout | 352171 | 3 | Vegetation Tree Non-Preventable | 2018-06-14 20:22 | OH | 13 | TRUE | 2018-08-02 | FALSE | TRUE | E | Patrol needed. Check arrestors and consider more trimming. Bamboo removal between poles 47113 & 21169 was requested 7/2/18. Check if it is removed.8/10/18 | OSMAN, DANY, KRIS | Patrolled. Sent an email to Don Eyster for trimming. FUWO sent for low secondaries at house# 2230 and 2214. 8/20/18. Per Joe Wolf trimming cycle is coming soon to this lateral. | TRUE | 2018-08-29
21169-NONE5514 | 211 | Fuse | Cutout | 353034 | 3 | Vegetation Tree Preventable | 2018-07-02 06:43 | OH | 13 | TRUE | 2018-08-02 | FALSE | TRUE | E | Patrol needed. Check arrestors and consider more trimming. Bamboo removal between poles 47113 & 21169 was requested 7/2/18. Check if it is removed.8/10/18 | OSMAN, DANY, KRIS | Patrolled. Sent an email to Don Eyster for trimming. FUWO sent for low secondaries at house# 2230 and 2214. 8/20/18Per Joe Wolf trimming cycle is coming soon to this lateral. | TRUE | 2018-08-29
23928-NONE3769 | 1033 | Fuse | Cutout | 327229 | 3 | Vegetation Tree Non-Preventable | 2017-08-03 02:21 | OH | 18 | TRUE | 2018-08-02 | FALSE | TRUE | W | Same neighborhood of this device #32326-NONE238681. Downstream of pole# 23928 must be patrolled. Check coordination. Consider a wide tree trimming option. |  |  | FALSE
23928-NONE3769 | 1033 | Fuse | Cutout | 351377 | 3 | Vegetation Tree Non-Preventable | 2018-05-27 15:27 | OH | 83 | TRUE | 2018-08-02 | FALSE | TRUE | W | Same neighborhood of this device #32326-NONE238681. Downstream of pole# 23928 must be patrolled. Check coordination. Consider a wide tree trimming option. |  |  | FALSE
23928-NONE3769 | 1033 | Fuse | Cutout | 354456 | 3 | Unknown | 2018-07-31 07:36 | OH | 85 | TRUE | 2018-08-02 | FALSE | TRUE | W | Same neighborhood of this device #32326-NONE238681. Downstream of pole# 23928 must be patrolled. Check coordination. Consider a wide tree trimming option. |  |  | FALSE
24440-NONE3913 | 1033 | Fuse | Cutout | 328133 | 3 | Unknown | 2017-08-26 00:26 | OH | 24 | TRUE | 2018-08-02 | FALSE | TRUE | W |  | Covered |  | TRUE | 2018-03-14
24440-NONE3913 | 1033 | Fuse | Cutout | 351421 | 3 | Weather Lighting | 2018-05-28 15:01 | OH | 82 | TRUE | 2018-08-02 | FALSE | TRUE | W | from Milvia's table | Johnny/Milvia | "Add animal package, evaluate wood pole Referred to T&D 5/31/18" | TRUE | 2018-03-14
24440-NONE3913 | 1033 | Fuse | Cutout | 353860 | 3 | Weather Lighting | 2018-07-22 14:49 | OH | 82 | TRUE | 2018-08-02 | FALSE | TRUE | W | This should be checked |  |  | TRUE | 2018-03-14
29848-NONE9347 | 1034 | Fuse | Cutout | 339508 | 3 | Vegetation Tree Non-Preventable | 2017-10-04 12:45 | OH | 4 | TRUE | 2018-08-02 | FALSE | TRUE | W |  | Covered |  | TRUE | 2018-03-14
29848-NONE9347 | 1034 | Fuse | Cutout | 345909 | 3 | Vegetation Tree Non-Preventable | 2018-01-25 11:16 | OH | 4 | TRUE | 2018-08-02 | FALSE | TRUE | W |  | Covered |  | TRUE | 2018-03-14
29848-NONE9347 | 1034 | Fuse | Cutout | 349228 | 3 | Equip Fail Other See Remarks | 2018-04-10 17:41 | OH | 4 | TRUE | 2018-08-02 | FALSE | TRUE | W | from Milvia's table | Covered | PATROL 4/16/18 | TRUE | 2018-03-14
29930-NONE5150 | 1034 | Fuse | Cutout | 339235 | 3 | Vegetation Tree Non-Preventable | 2017-10-01 06:23 | OH | 4 | TRUE | 2018-08-02 | FALSE | TRUE | W | from Milvia's table | Covered |  | TRUE | 2018-03-14
29930-NONE5150 | 1034 | Fuse | Cutout | 339402 | 3 | Vegetation Tree Non-Preventable | 2017-10-03 12:17 | OH | 4 | TRUE | 2018-08-02 | FALSE | TRUE | W | from Milvia's table | Covered |  | TRUE | 2018-03-14
29930-NONE5150 | 1034 | Fuse | Cutout | 352839 | 3 | Vegetation Tree Non-Preventable | 2018-06-27 16:50 | OH | 4 | TRUE | 2018-08-02 | FALSE | TRUE | W | from Milvia's table | Fuesha & Kristin |  | TRUE | 2018-03-14
32326-NONE238681 | 1033 | Fuse | Cutout | 342367 | 3 | Weather Wind | 2017-12-12 15:01 | OH | 76 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol for trees and arrestors. 65ks and 40ks fuses may not be working well. Look for higher than 65ks fuse option at pole#32326 or lower than 40ks fuse option for downstream. |  |  | FALSE
32326-NONE238681 | 1033 | Fuse | Cutout | 346875 | 3 | Vegetation Tree Non-Preventable | 2018-02-26 23:36 | OH | 76 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol for trees and arrestors. 65ks and 40ks fuses may not be working well. Look for higher than 65ks fuse option at pole#32326 or lower than 40ks fuse option for downstream. |  |  | FALSE
32326-NONE238681 | 1033 | Fuse | Cutout | 351737 | 3 | Equip Fail Arrestor | 2018-06-05 02:53 | OH | 76 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol for trees and arrestors. 65ks and 40ks fuses may not be working well. Look for higher than 65ks fuse option at pole#32326 or lower than 40ks fuse option for downstream. |  |  | FALSE
33071-FX7419/1 | 1431 | Fuse | Cutout Terminating | 340824 | 3 | Equip Fail Other See Remarks | 2017-10-29 06:36 | UG | 4 | TRUE | 2018-08-02 | FALSE | TRUE | E | Known incident.Nothing to do |  |  | TRUE | 2018-08-13
33071-FX7419/1 | 1431 | Fuse | Cutout Terminating | 340887 | 3 | Equip Fail Other See Remarks | 2017-10-31 09:50 | UG | 2 | TRUE | 2018-08-02 | FALSE | TRUE | E | Known incident.Nothing to do |  |  | TRUE | 2018-08-13
33071-FX7419/1 | 1431 | Fuse | Cutout Terminating | 341831 | 3 | Equip Fail Other See Remarks | 2017-11-27 23:34 | UG | 2 | TRUE | 2018-08-02 | FALSE | TRUE | E | Known incident.Nothing to do |  |  | TRUE | 2018-08-13
35336-RCL258 | 539 | Recloser | OH Three Phase Recloser | 342347 | 3 | Equip Fail OH Primary | 2017-12-12 12:04 | OH | 82 | TRUE | 2018-08-02 | FALSE | TRUE | W | This recloser is having many outages. Is this a 3 phase recloser or are there 3 single phase relosers? Patrol needed. |  |  | FALSE
35336-RCL258 | 539 | Recloser | OH Three Phase Recloser | 351828 | 3 | Weather Lighting | 2018-06-06 13:37 | OH | 82 | TRUE | 2018-08-02 | FALSE | TRUE | W | This recloser is having many outages. Is this a 3 phase recloser or are there 3 single phase relosers? Patrol needed. |  |  | FALSE
35336-RCL258 | 539 | Recloser | OH Three Phase Recloser | 353863 | 3 | Weather NWS Tornado | 2018-07-22 13:24 | OH | 81 | TRUE | 2018-08-02 | FALSE | TRUE | W | This recloser is having many outages. Is this a 3 phase recloser or are there 3 single phase relosers? Patrol needed. |  |  | FALSE
47315-FX3103R0 | 203 | Fuse | Cutout Terminating | 338825 | 3 | Human Other See Remarks | 2017-09-25 10:01 | UG | 92 | TRUE | 2018-08-02 | FALSE | TRUE | E | Human cause, accident | OSMAN | nothing to do | FALSE
47315-FX3103R0 | 203 | Fuse | Cutout Terminating | 344022 | 3 | Equip Fail Other See Remarks | 2018-01-18 06:34 | UG | 91 | TRUE | 2018-08-02 | FALSE | TRUE | E | This is a very big lateral with 299 customers. Coordination must be checked. Segmentation may be needed. Patrol. | OSMAN | Patrolled half. Fuse coordination needed. Many broken ground wire found. Blown arrestor and old areestor found. Some vines sprayed and more needed.8/23/18 patrol finished 8/24/18 | FALSE
47315-FX3103R0 | 203 | Fuse | Cutout Terminating | 350809 | 3 | Weather Lighting | 2018-05-15 14:45 | UG | 91 | TRUE | 2018-08-02 | FALSE | TRUE | E | This is a very big lateral with 299 customers. Coordination must be checked. Segmentation may be needed. Patrol. | OSMAN | Patrolled half. Fuse coordination needed. Many broken ground wire found. Blown arrestor and old areestor found. Some vines sprayed and more needed.8/23/18 patrol finished 8/24/18 | FALSE
63736-FX229D/6 | 213 | Fuse | Padmount Fuse | 340661 | 3 | Equip Fail OH Primary | 2017-10-24 18:11 | UG | 11 | TRUE | 2018-08-02 | FALSE | TRUE | E | Patrol needed | OSMAN, DANY, KRIS | Patrolled. No action taken. | TRUE | 2018-08-20
63736-FX229D/6 | 213 | Fuse | Padmount Fuse | 352041 | 3 | Weather Lighting | 2018-06-11 16:29 | UG | 11 | TRUE | 2018-08-02 | FALSE | TRUE | E | Patrol needed | OSMAN, DANY, KRIS | Patrolled. No action taken. | TRUE | 2018-08-20
63736-FX229D/6 | 213 | Fuse | Padmount Fuse | 352059 | 3 | Weather Lighting | 2018-06-11 18:39 | UG | 10 | TRUE | 2018-08-02 | FALSE | TRUE | E | Patrol needed | OSMAN, DANY, KRIS | Patrolled. No action taken. | TRUE | 2018-08-20
64524-FX9228/4 | 1531 | Fuse | Padmount Fuse | 339179 | 3 | Unknown | 2017-09-30 06:40 | UG | 3 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol needed. Consider putting an overhead cutout so that we eliminate replacing E fuses. E fuse is much more expensive than K or KS. |  |  | FALSE
64524-FX9228/4 | 1531 | Fuse | Padmount Fuse | 340264 | 3 | Vegetation Vines | 2017-10-13 03:27 | UG | 3 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol needed. Consider putting an overhead cutout so that we eliminate replacing E fuses. E fuse is much more expensive than K or KS. |  |  | FALSE
64524-FX9228/4 | 1531 | Fuse | Padmount Fuse | 340338 | 3 | Equip Fail Arrestor | 2017-10-15 02:19 | UG | 3 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol needed. Consider putting an overhead cutout so that we eliminate replacing E fuses. E fuse is much more expensive than K or KS. |  |  | FALSE
75681-FX9380/1 | 551 | Fuse | Cutout Terminating | 339803 | 3 | Unknown | 2017-10-08 01:19 | UG | 413 | TRUE | 2018-08-02 | FALSE | TRUE | E | I believe; per Charlie frogs caused outages one after another. Engineering did not want to install fault indicator however linemen did. | OSMAN, RICKY | Patrolled with thermal camera. Nothing found. | TRUE | 2017-12-20
75681-FX9380/1 | 551 | Fuse | Cutout Terminating | 339963 | 3 | Unknown | 2017-10-09 18:55 | UG | 354 | TRUE | 2018-08-02 | FALSE | TRUE | E | I believe; per Charlie frogs caused outages one after another. Engineering did not want to install fault indicator however linemen did. | OSMAN, RICKY | Patrolled with thermal camera. Nothing found. | TRUE | 2017-12-20
75681-FX9380/1 | 551 | Fuse | Cutout Terminating | 342685 | 3 | Animal Other See Remarks | 2017-12-20 17:24 | UG | 790 | TRUE | 2018-08-02 | FALSE | TRUE | E | I believe; per Charlie frogs caused outages one after another. Engineering did not want to install fault indicator however linemen did. | OSMAN, RICKY | Patrolled with thermal camera. Nothing found. | TRUE | 2017-12-20
93903-RCL268 | 540 | Recloser | OH Three Phase Recloser | 327620 | 4 | Weather Lighting | 2017-08-09 03:42 | OH | 607 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol and see how can we trim further. This part of circuit 540 is along with milhopper scenic road. A wide trimming can be helpful. We should insist for a wide trimming. |  |  | FALSE
93903-RCL268 | 540 | Recloser | OH Three Phase Recloser | 327871 | 4 | Weather Lighting | 2017-08-18 13:18 | OH | 219 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol and see how can we trim further. This part of circuit 540 is along with milhopper scenic road. A wide trimming can be helpful. We should insist for a wide trimming. |  |  | FALSE
93903-RCL268 | 540 | Recloser | OH Three Phase Recloser | 327938 | 4 | Vegetation Tree Non-Preventable | 2017-08-18 19:45 | OH | 219 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol and see how can we trim further. This part of circuit 540 is along with milhopper scenic road. A wide trimming can be helpful. We should insist for a wide trimming. |  |  | FALSE
93903-RCL268 | 540 | Recloser | OH Three Phase Recloser | 327923 | 4 | Vegetation Tree Non-Preventable | 2017-08-18 22:26 | OH | 219 | TRUE | 2018-08-02 | FALSE | TRUE | W | Patrol and see how can we trim further. This part of circuit 540 is along with milhopper scenic road. A wide trimming can be helpful. We should insist for a wide trimming. |  |  | FALSE
34468-NONE40481 | 434 | Fuse | Cutout | 346553 | 3 | Equip Fail UG Direct Buried | 2018-02-17 07:52 | OH | 12 | FALSE | 2018-08-28 | FALSE | TRUE | E |  |  |  | FALSE
34468-NONE40481 | 434 | Fuse | Cutout | 354971 | 3 | Human Other See Remarks | 2018-08-14 11:18 | OH | 8 | FALSE | 2018-08-28 | FALSE | TRUE | E |  |  |  | FALSE
36838-RCL270 | 1034 | Recloser | OH Three Phase Recloser | 347443 | 3 | Vegetation Tree Non-Preventable | 2018-03-19 06:48 | OH | 1077 | TRUE | 2018-08-28 | FALSE | TRUE | W | It is all related trimming. limb at pole 22565. limb at pole 23676. limb at pole 24725. many customer complains |  |  | FALSE
36838-RCL270 | 1034 | Recloser | OH Three Phase Recloser | 347657 | 3 | Vegetation Tree Non-Preventable | 2018-03-19 09:55 | OH | 1067 | TRUE | 2018-08-28 | FALSE | TRUE | W | Check if trimming needed. LIMB FOUND IN PHASES AT POLE 20101, many customer complains |  |  | FALSE
36838-RCL270 | 1034 | Recloser | OH Three Phase Recloser | 355252 | 3 | Weather Lighting | 2018-08-18 17:36 | OH | 1099 | TRUE | 2018-08-28 | FALSE | TRUE | W | Check if more arresters needed? Static was down around POLE # 24726. Ricky checked arresters. Nothing found. 8/29/18 |  |  | FALSE
21676-FX3150R0 | 217 | Fuse | Cutout Terminating | 355713 | 2 | Equip Fail Other See Remarks | 2018-08-29 08:30 | UG | 24 | FALSE | 2018-09-04 | TRUE | FALSE |  |  |  |  | FALSE
21676-FX3150R0 | 217 | Fuse | Cutout Terminating | 355939 | 2 | Vegetation Tree Non-Preventable | 2018-08-31 19:12 | UG | 15 | FALSE | 2018-09-04 | TRUE | FALSE |  |  |  |  | FALSE
29848-NONE9347 | 1034 | Fuse | Cutout | 355733 | 4 | Vegetation Tree Non-Preventable | 2018-08-29 13:48 | OH | 4 | FALSE | 2018-09-04 | FALSE | TRUE |  |  |  |  | FALSE